## System Calculation
SYSTEM CALCULATOR DETNOV CAD-150 EXCEL TOOL | [8 empty] | SC 116 en 2019 f
Fill the field for the maximum % of devices in alarm at the same time (Yelow field)
Time backup power supply | [6 empty] | Maximum devices in alarm at the same time
Standby time | 72 | h | Select standby time |  |  |  | Detectors | Max.10/loop
Alarm time | 30 | min | Select alarm time |  |  |  | MCP | 10%
[7 empty] | Sounders/Strobes | 50%
System Parameters | [6 empty] | Modules | 50%
| #N/A | #N/A | Select control panel from the list
| 0 | 0 | Select battery from the list
| I_Standby (A) | I_Alarm (A)
Panel auxilliary 24VCC output
Panel sounder output 1
Pantel sounder output 2
I_Total_Standby | #N/A | A |  | Minimum battery needed |  |  | Battery Time*
I_Total_Alarm | #N/A | A |  | #N/A |  |  | 2 x 7,2 Ah | 2 x 12 Ah** | 2 x 18 Ah | 2 x 24 Ah
1,25 Cmin | #N/A | #N/A | #N/A |  |  |  | #N/A | #N/A | #N/A | #N/A
Selected battery | #N/A | #N/A | #N/A |  |  |  | *Battery time: Standby time + Alarm mode time
| #N/A |  |  | #N/A |  |  | **BTD-1212 only available for CAD-150-2-MB and CAD-150-4
Fill the PCS field if panel has extension card (Yellow field)
Loop | I_Standby (A) | I_Alarm (A) |  | Extension Cards | PCS | I_Standby (A) | I_Standby (A)
Loop 1 | 0 | 0 |  | TRED-150 | 0 | 0.05 | 0
Loop 2 | 0 | 0 |  | TMB-151 | 0 | 0.05 | 0
Loop 3 | 0 | 0 |  | TMBFI-151 | 0 | 0.05 | 0
Loop 4 | 0 | 0 |  | TMB-251 | 0 | 0.05 | 0
Loop 5 | 0 | 0 |  | TMBFI-251 | 0 | 0.05 | 0
Loop 6 | 0 | 0 |  | TED-151-CL | 0 | 0.05 | 0
Loop 7 | 0 | 0 |  |  | 0 |  | 0
Loop 8 | 0 | 0
Total | 0 | 0
This tool may be used as a design help for Detnov Security S.L. We reserve the right not to be responsible for its accuracy, completeness or quality of the information provided, including any kind of information which could be incomplete or incorrect.

## Datos (hidden)
Características centrales |  |  |  | Características baterías
Central |  | I_Reposo (A) | I_Alarma (A) |  | Voltaje (V) | Capacidad (Ah) |  |  | TABLA AUXILIAR
CAD-150-1 & CAD-150-1-Mini | CAD_150_1 | 0.16 | 0.2 | BTD-1207 | 12 | 7.2 | 24 | BTD-1224 | Centrales
CAD-150-2 | CAD_150_2 | 0.22 | 0.255 | BTD-1212 | 12 | 12 | 18 | BTD-1218 |  | CAD_150_1 | CAD_150_2 | CAD_150_2_MB | CAD_150_4 | CAD_150_8_4loop | CAD_150_8_6loop | CAD_150_8_8loop | CAD_150_8PLUS_4loop | CAD_150_8PLUS_6loop | CAD_150_8PLUS_8loop | CAD_150_4_P | CAD_150_8PLUS_P_4loop | CAD_150_8PLUS_P_6loop | CAD_150_8PLUS_P_8loop
CAD-150-2-MB | CAD_150_2_MB | 0.26 | 0.3 | BTD-1218 | 12 | 18 | 12 | BTD-1212 | CAD_150_1 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207 | BTD-1207
CAD-150-4 | CAD_150_4 | 0.3 | 0.34 | BTD-1224 | 12 | 24 | 7.2 | BTD-1207 | CAD_150_2 |  |  | BTD-1212 | BTD-1212 | BTD-1218 | BTD-1218 | BTD-1218 | BTD-1218 | BTD-1218 | BTD-1218 |  | BTD-1218 | BTD-1218 | BTD-1218
CAD-150-8 (4 lazos) | CAD_150_8_4loop | 0.3 | 0.34 | [5 empty] | CAD_150_2_MB | [7 empty] | BTD-1224 | BTD-1224 | BTD-1224 |  | BTD-1224 | BTD-1224 | BTD-1224
CAD-150-8 (6 lazos) | CAD_150_8_6loop | 0.4 | 0.44 | [5 empty] | CAD_150_4
CAD-150-8 (8 lazos) | CAD_150_8_8loop | 0.5 | 0.54 | Características baterías |  |  |  |  | CAD_150_8_4loop
CAD-150-8-PLUS (4 lazos) | CAD_150_8PLUS_4loop | 0.3 | 0.34 | Cantidad tarjetas |  |  |  |  | CAD_150_8_6loop
CAD-150-8-PLUS (6 lazos) | CAD_150_8PLUS_6loop | 0.4 | 0.44 | 0 |  |  |  |  | CAD_150_8_8loop
CAD-150-8-PLUS (8 lazos) | CAD_150_8PLUS_8loop | 0.5 | 0.54 | 1 |  |  |  |  | CAD_150_8PLUS_4loop
CAD-150-4-P | CAD_150_4_P | 0.335 | 0.375 | [5 empty] | CAD_150_8PLUS_6loop
CAD-150-8-PLUS-P (4 lazos) | CAD_150_8PLUS_P_4loop | 0.335 | 0.375 | Sección cable |  |  |  |  | CAD_150_8PLUS_8loop
CAD-150-8-PLUS-P (6 lazos) | CAD_150_8PLUS_P_6loop | 0.435 | 0.475 | 0.8 |  |  |  |  | CAD_150_4_P
CAD-150-8-PLUS-P (8 lazos) | CAD_150_8PLUS_P_8loop | 0.535 | 0.575 | 1 |  |  |  |  | CAD_150_8PLUS_P_4loop
|  |  |  | 1.5 |  |  |  |  | CAD_150_8PLUS_P_6loop
|  | Tiempos según normativa |  | 2 |  |  |  |  | CAD_150_8PLUS_P_8loop
|  | Reposo (h) | Alarma (min) | 2.5
|  | 72 | 30 | [5 empty] | TABLA AUXILIAR 2: para condición de batería necesaria
|  | 48 | 15
|  | 30 | 5 | [5 empty] | Centrales
|  | 24 | 0 | Fuentes alimentación: |  |  |  |  | CAD_150_1 | BTD-1207
|  | 4 |  | 120 | FAD-150 |  |  |  | CAD_150_2 | BTD-1207
|  |  |  | 38 | FAD-40 |  |  |  | CAD_150_2_MB | BTD-1207
|  |  |  | 17 | TUL375 EN |  |  |  | CAD_150_4 | BTD-1207
[9 empty] | CAD_150_8_4loop | BTD-1207 | BTD-1218
|  |  |  | 0 | #N/A | #N/A |  |  | CAD_150_8_6loop | BTD-1207 | BTD-1218
|  |  |  | 0 | #N/A | #N/A |  |  | CAD_150_8_8loop | BTD-1207 | BTD-1218
[9 empty] | CAD_150_8PLUS_4loop | BTD-1207 | BTD-1218 | BTD-1224
|  |  |  | Minimum battery needed |  | Dif. Entre BTD y Minimum battery needed |  |  | CAD_150_8PLUS_6loop | BTD-1207 | BTD-1218 | BTD-1224
|  |  |  | #N/A |  | #N/A | #N/A |  | CAD_150_8PLUS_8loop | BTD-1207 | BTD-1218 | BTD-1224
[6 empty] | PS necesaria: | #N/A |  | CAD_150_4_P | BTD-1207
[9 empty] | CAD_150_8PLUS_P_4loop | BTD-1207 | BTD-1218 | BTD-1224
[9 empty] | CAD_150_8PLUS_P_6loop | BTD-1207 | BTD-1218 | BTD-1224
[9 empty] | CAD_150_8PLUS_P_8loop | BTD-1207 | BTD-1218 | BTD-1224
Para ocultar valores en celda: formato de numero. En el cuadro tipo escribir ;;; (3 puntos y coma)

## SC_Loop 1
SYSTEM CALCULATOR DETNOV CAD-150 EXCEL TOOL | [10 empty] | SC 116 en 2019 f
Loop | [8 empty] | System Check
Section of wire | 1.5 |  | mm2 | [5 empty] | Current |  | OK
Lenght loop | 2000 |  | meters | [5 empty] | Addresses |  | OK
Fill Cable Section in mm2 and the Line Distance in meters (Yelow field)
| Fill the PCS field for the desired configuration (Yelow field) | Fill the PCS field for the desired configuration (Yelow field)
Devices Loop 1
REF. | PCS | I_Standby (A) | I_Standby (A) | PCS_alarm | I_Alarm (A) | I_Alarm (A) | I_Sounders (A) | DET | MOD | SND | ADR
DOD-220A |  | 0.0003 | 0 | 0 | 0.003 | 0
DOD-220A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DOTD-230A |  | 0.0003 | 0 | 0 | 0.003 | 0
DOTD-230A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-210A |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-210A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-215A |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-215A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DGD-600 |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-600-AC |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-620 |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-620-AC |  | 0.00091 | 0 | 0 | 0.0011 | 0
MAD-401 & MAD-401-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-402 & MAD-402-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-405-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-409-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-411 & MAD-411-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-412 & MAD-412-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-415-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-419-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-421 & MAD-421-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-422 & MAD-422-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-425-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-429-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-431 & MAD-431-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-432 & MAD-432-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-441 & MAD-441-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-442 & MAD-442-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-450 & MAD-450-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-451-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-461-I |  | 0.0003 | 0 | 0 | 0.009 | 0
MAD-464-I Low vol. (78 dB) |  | 0.0003 | 0 | 0 | 0.0065 | 0
MAD-464-I Medium vol. (93 dB) |  | 0.0003 | 0 | 0 | 0.0097 | 0
MAD-464-I High vol. (97 dB) |  | 0.0003 | 0 | 0 | 0.013 | 0
MAD-465-I Low vol. (78 dB) |  | 0.0003 | 0 | 0 | 0.0065 | 0
MAD-465-I Medium vol. (93 dB) |  | 0.0003 | 0 | 0 | 0.0097 | 0
MAD-465-I High vol. (97 dB) |  | 0.0003 | 0 | 0 | 0.013 | 0
MAD-472 |  | 0.00035 | 0 | 0 | 0.014 | 0
MAD-473 |  | 0.00035 | 0 | 0 | 0.015 | 0
MAD-481 |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-490 |  | 0.0003 | 0 |  | 0.05 | 0
PAD-10 |  | 0.000625 | 0 | 0 | 0.005 | 0
PAD-10A-I |  | 0.000185 | 0 | 0 | 0.004 | 0
TPLD-100 (CCD-102) = 3 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-104) = 5 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-108) = 9 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-112) = 13 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-103) = 7 loop address |  | 0.0003 | 0 |  | 0.003 | 0
Total | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
Loop Parameters
Cu | 0.0172 |  | Ω*mm2/m
I_Standby | 0 |  | A
I_Alarm | 0 |  | A
I_Sounders | 0 |  | A
I_Total | 0 |  | A
V_Lin_Ring | 6.9 |  | V
Minimum Cable Section for common Lenghts | [10 empty] | Warning: The Minimum Cable Seccion in the Loop is 0,5 mm2
Lenghts | 1000 |  | 1500 |  |  | 2000 | 2500 | 3000 | 3500 | m
R_Cable | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
S_min | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | mm2
Maximum Cable Lenght for Standard Cable Section (IEC 60228) | [10 empty] | Warning: The Maximum Cable Length in the Loop is 3500 meters
Section | 0.5 |  | 0.75 |  |  | 1 | 1.5 | 2.5 | 4 | mm2
R_Cable | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
L_max | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | m
Maximum Current Calculation
? S | 1.5 |  | mm2
? L | 2000 |  | mm2
R_Cable_Sys | 45.8667 |  | Ω
R_eq_Ring_Sys | 22.9333 |  | Ω
I_max | 0.30087 |  | A
System Check
Current |  |  | OK
Addresses |  |  | OK
This tool may be used as a design help for Detnov Security S.L. We reserve the right not to be responsible for its accuracy, completeness or quality of the information provided, including any kind of information which could be incomplete or incorrect.

## SC_Loop 2
SYSTEM CALCULATOR DETNOV CAD-150 EXCEL TOOL | [10 empty] | SC 116 en 2019 f
Loop | [8 empty] | System Check
Section of wire | 1.5 |  | mm2 | [5 empty] | Current |  | OK
Lenght loop | 2000 |  | meters | [5 empty] | Addresses |  | OK
Fill Cable Section in mm2 and the Line Distance in meters (Yelow field)
| Fill the PCS field for the desired configuration (Yelow field) | Fill the PCS field for the desired configuration (Yelow field)
Devices Loop 2
REF. | PCS | I_Standby (A) | I_Standby (A) | PCS_alarm | I_Alarm (A) | I_Alarm (A) | I_Sounders (A) | DET | MOD | SND | ADR
DOD-220A |  | 0.0003 | 0 | 0 | 0.003 | 0
DOD-220A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DOTD-230A |  | 0.0003 | 0 | 0 | 0.003 | 0
DOTD-230A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-210A |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-210A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-215A |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-215A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DGD-600 |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-600-AC |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-620 |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-620-AC |  | 0.00091 | 0 | 0 | 0.0011 | 0
MAD-401 & MAD-401-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-402 & MAD-402-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-405-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-409-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-411 & MAD-411-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-412 & MAD-412-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-415-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-419-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-421 & MAD-421-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-422 & MAD-422-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-425-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-429-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-431 & MAD-431-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-432 & MAD-432-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-441 & MAD-441-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-442 & MAD-442-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-450 & MAD-450-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-451-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-461-I |  | 0.0003 | 0 | 0 | 0.009 | 0
MAD-464-I Low vol. (78 dB) |  | 0.0003 | 0 | 0 | 0.0065 | 0
MAD-464-I Medium vol. (93 dB) |  | 0.0003 | 0 | 0 | 0.0097 | 0
MAD-464-I High vol. (97 dB) |  | 0.0003 | 0 | 0 | 0.013 | 0
MAD-465-I Low vol. (78 dB) |  | 0.0003 | 0 | 0 | 0.0065 | 0
MAD-465-I Medium vol. (93 dB) |  | 0.0003 | 0 | 0 | 0.0097 | 0
MAD-465-I High vol. (97 dB) |  | 0.0003 | 0 | 0 | 0.013 | 0
MAD-472 |  | 0.00035 | 0 | 0 | 0.014 | 0
MAD-473 |  | 0.00035 | 0 | 0 | 0.015 | 0
MAD-481 |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-490 |  | 0.0003 | 0 |  | 0.05 | 0
PAD-10 |  | 0.000625 | 0 | 0 | 0.005 | 0
PAD-10A-I |  | 0.000185 | 0 | 0 | 0.004 | 0
TPLD-100 (CCD-102) = 3 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-104) = 5 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-108) = 9 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-112) = 13 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-103) = 7 loop address |  | 0.0003 | 0 |  | 0.003 | 0
Total | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
Loop Parameters
Cu | 0.0172 |  | Ω*mm2/m
I_Standby | 0 |  | A
I_Alarm | 0 |  | A
I_Sounders | 0 |  | A
I_Total | 0 |  | A
V_Lin_Ring | 6.9 |  | V
Minimum Cable Section for common Lenghts | [10 empty] | Warning: The Minimum Cable Seccion in the Loop is 0,5 mm2
Lenghts | 1000 |  | 1500 |  |  | 2000 | 2500 | 3000 | 3500 | m
R_Cable | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
S_min | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | mm2
Maximum Cable Lenght for Standard Cable Section (IEC 60228) | [10 empty] | Warning: The Maximum Cable Length in the Loop is 3500 meters
Section | 0.5 |  | 0.75 |  |  | 1 | 1.5 | 2.5 | 4 | mm2
R_Cable | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
L_max | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | m
Maximum Current Calculation
? S | 1.5 |  | mm2
? L | 2000 |  | mm2
R_Cable_Sys | 45.8667 |  | Ω
R_eq_Ring_Sys | 22.9333 |  | Ω
I_max | 0.30087 |  | A
System Check
Current |  |  | OK
Addresses |  |  | OK
This tool may be used as a design help for Detnov Security S.L. We reserve the right not to be responsible for its accuracy, completeness or quality of the information provided, including any kind of information which could be incomplete or incorrect.

## SC_Loop 3
SYSTEM CALCULATOR DETNOV CAD-150 EXCEL TOOL | [10 empty] | SC 116 en 2019 f
Loop | [8 empty] | System Check
Section of wire | 1.5 |  | mm2 | [5 empty] | Current |  | OK
Lenght loop | 2000 |  | meters | [5 empty] | Addresses |  | OK
Fill Cable Section in mm2 and the Line Distance in meters (Yelow field)
| Fill the PCS field for the desired configuration (Yelow field) | Fill the PCS field for the desired configuration (Yelow field)
Devices Loop 3
REF. | PCS | I_Standby (A) | I_Standby (A) | PCS_alarm | I_Alarm (A) | I_Alarm (A) | I_Sounders (A) | DET | MOD | SND | ADR
DOD-220A |  | 0.0003 | 0 | 0 | 0.003 | 0
DOD-220A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DOTD-230A |  | 0.0003 | 0 | 0 | 0.003 | 0
DOTD-230A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-210A |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-210A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-215A |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-215A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DGD-600 |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-600-AC |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-620 |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-620-AC |  | 0.00091 | 0 | 0 | 0.0011 | 0
MAD-401 & MAD-401-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-402 & MAD-402-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-405-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-409-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-411 & MAD-411-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-412 & MAD-412-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-415-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-419-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-421 & MAD-421-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-422 & MAD-422-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-425-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-429-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-431 & MAD-431-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-432 & MAD-432-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-441 & MAD-441-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-442 & MAD-442-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-450 & MAD-450-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-451-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-461-I |  | 0.0003 | 0 | 0 | 0.009 | 0
MAD-464-I Low vol. (78 dB) |  | 0.0003 | 0 | 0 | 0.0065 | 0
MAD-464-I Medium vol. (93 dB) |  | 0.0003 | 0 | 0 | 0.0097 | 0
MAD-464-I High vol. (97 dB) |  | 0.0003 | 0 | 0 | 0.013 | 0
MAD-465-I Low vol. (78 dB) |  | 0.0003 | 0 | 0 | 0.0065 | 0
MAD-465-I Medium vol. (93 dB) |  | 0.0003 | 0 | 0 | 0.0097 | 0
MAD-465-I High vol. (97 dB) |  | 0.0003 | 0 | 0 | 0.013 | 0
MAD-472 |  | 0.00035 | 0 | 0 | 0.014 | 0
MAD-473 |  | 0.00035 | 0 | 0 | 0.015 | 0
MAD-481 |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-490 |  | 0.0003 | 0 |  | 0.05 | 0
PAD-10 |  | 0.000625 | 0 | 0 | 0.005 | 0
PAD-10A-I |  | 0.000185 | 0 | 0 | 0.004 | 0
TPLD-100 (CCD-102) = 3 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-104) = 5 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-108) = 9 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-112) = 13 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-103) = 7 loop address |  | 0.0003 | 0 |  | 0.003 | 0
Total | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
Loop Parameters
Cu | 0.0172 |  | Ω*mm2/m
I_Standby | 0 |  | A
I_Alarm | 0 |  | A
I_Sounders | 0 |  | A
I_Total | 0 |  | A
V_Lin_Ring | 6.9 |  | V
Minimum Cable Section for common Lenghts | [10 empty] | Warning: The Minimum Cable Seccion in the Loop is 0,5 mm2
Lenghts | 1000 |  | 1500 |  |  | 2000 | 2500 | 3000 | 3500 | m
R_Cable | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
S_min | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | mm2
Maximum Cable Lenght for Standard Cable Section (IEC 60228) | [10 empty] | Warning: The Maximum Cable Length in the Loop is 3500 meters
Section | 0.5 |  | 0.75 |  |  | 1 | 1.5 | 2.5 | 4 | mm2
R_Cable | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
L_max | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | m
Maximum Current Calculation
? S | 1.5 |  | mm2
? L | 2000 |  | mm2
R_Cable_Sys | 45.8667 |  | Ω
R_eq_Ring_Sys | 22.9333 |  | Ω
I_max | 0.30087 |  | A
System Check
Current |  |  | OK
Addresses |  |  | OK
This tool may be used as a design help for Detnov Security S.L. We reserve the right not to be responsible for its accuracy, completeness or quality of the information provided, including any kind of information which could be incomplete or incorrect.

## SC_Loop 4
SYSTEM CALCULATOR DETNOV CAD-150 EXCEL TOOL | [10 empty] | SC 116 en 2019 f
Loop | [8 empty] | System Check
Section of wire | 1.5 |  | mm2 | [5 empty] | Current |  | OK
Lenght loop | 2000 |  | meters | [5 empty] | Addresses |  | OK
Fill Cable Section in mm2 and the Line Distance in meters (Yelow field)
| Fill the PCS field for the desired configuration (Yelow field) | Fill the PCS field for the desired configuration (Yelow field)
Devices Loop 4
REF. | PCS | I_Standby (A) | I_Standby (A) | PCS_alarm | I_Alarm (A) | I_Alarm (A) | I_Sounders (A) | DET | MOD | SND | ADR
DOD-220A |  | 0.0003 | 0 | 0 | 0.003 | 0
DOD-220A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DOTD-230A |  | 0.0003 | 0 | 0 | 0.003 | 0
DOTD-230A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-210A |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-210A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-215A |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-215A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DGD-600 |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-600-AC |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-620 |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-620-AC |  | 0.00091 | 0 | 0 | 0.0011 | 0
MAD-401 & MAD-401-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-402 & MAD-402-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-405-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-409-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-411 & MAD-411-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-412 & MAD-412-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-415-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-419-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-421 & MAD-421-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-422 & MAD-422-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-425-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-429-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-431 & MAD-431-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-432 & MAD-432-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-441 & MAD-441-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-442 & MAD-442-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-450 & MAD-450-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-451-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-461-I |  | 0.0003 | 0 | 0 | 0.009 | 0
MAD-464-I Low vol. (78 dB) |  | 0.0003 | 0 | 0 | 0.0065 | 0
MAD-464-I Medium vol. (93 dB) |  | 0.0003 | 0 | 0 | 0.0097 | 0
MAD-464-I High vol. (97 dB) |  | 0.0003 | 0 | 0 | 0.013 | 0
MAD-465-I Low vol. (78 dB) |  | 0.0003 | 0 | 0 | 0.0065 | 0
MAD-465-I Medium vol. (93 dB) |  | 0.0003 | 0 | 0 | 0.0097 | 0
MAD-465-I High vol. (97 dB) |  | 0.0003 | 0 | 0 | 0.013 | 0
MAD-472 |  | 0.00035 | 0 | 0 | 0.014 | 0
MAD-473 |  | 0.00035 | 0 | 0 | 0.015 | 0
MAD-481 |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-490 |  | 0.0003 | 0 |  | 0.05 | 0
PAD-10 |  | 0.000625 | 0 | 0 | 0.005 | 0
PAD-10A-I |  | 0.000185 | 0 | 0 | 0.004 | 0
TPLD-100 (CCD-102) = 3 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-104) = 5 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-108) = 9 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-112) = 13 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-103) = 7 loop address |  | 0.0003 | 0 |  | 0.003 | 0
Total | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
Loop Parameters
Cu | 0.0172 |  | Ω*mm2/m
I_Standby | 0 |  | A
I_Alarm | 0 |  | A
I_Sounders | 0 |  | A
I_Total | 0 |  | A
V_Lin_Ring | 6.9 |  | V
Minimum Cable Section for common Lenghts | [10 empty] | Warning: The Minimum Cable Seccion in the Loop is 0,5 mm2
Lenghts | 1000 |  | 1500 |  |  | 2000 | 2500 | 3000 | 3500 | m
R_Cable | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
S_min | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | mm2
Maximum Cable Lenght for Standard Cable Section (IEC 60228) | [10 empty] | Warning: The Maximum Cable Length in the Loop is 3500 meters
Section | 0.5 |  | 0.75 |  |  | 1 | 1.5 | 2.5 | 4 | mm2
R_Cable | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
L_max | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | m
Maximum Current Calculation
? S | 1.5 |  | mm2
? L | 2000 |  | mm2
R_Cable_Sys | 45.8667 |  | Ω
R_eq_Ring_Sys | 22.9333 |  | Ω
I_max | 0.30087 |  | A
System Check
Current |  |  | OK
Addresses |  |  | OK
This tool may be used as a design help for Detnov Security S.L. We reserve the right not to be responsible for its accuracy, completeness or quality of the information provided, including any kind of information which could be incomplete or incorrect.

## SC_Loop 5
SYSTEM CALCULATOR DETNOV CAD-150 EXCEL TOOL | [10 empty] | SC 116 en 2019 f
Loop | [8 empty] | System Check
Section of wire | 1.5 |  | mm2 | [5 empty] | Current |  | OK
Lenght loop | 2000 |  | meters | [5 empty] | Addresses |  | OK
Fill Cable Section in mm2 and the Line Distance in meters (Yelow field)
| Fill the PCS field for the desired configuration (Yelow field) | Fill the PCS field for the desired configuration (Yelow field)
Devices Loop 5
REF. | PCS | I_Standby (A) | I_Standby (A) | PCS_alarm | I_Alarm (A) | I_Alarm (A) | I_Sounders (A) | DET | MOD | SND | ADR
DOD-220A |  | 0.0003 | 0 | 0 | 0.003 | 0
DOD-220A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DOTD-230A |  | 0.0003 | 0 | 0 | 0.003 | 0
DOTD-230A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-210A |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-210A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-215A |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-215A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DGD-600 |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-600-AC |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-620 |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-620-AC |  | 0.00091 | 0 | 0 | 0.0011 | 0
MAD-401 & MAD-401-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-402 & MAD-402-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-405-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-409-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-411 & MAD-411-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-412 & MAD-412-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-415-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-419-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-421 & MAD-421-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-422 & MAD-422-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-425-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-429-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-431 & MAD-431-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-432 & MAD-432-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-441 & MAD-441-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-442 & MAD-442-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-450 & MAD-450-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-451-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-461-I |  | 0.0003 | 0 | 0 | 0.009 | 0
MAD-464-I Low vol. (78 dB) |  | 0.0003 | 0 | 0 | 0.0065 | 0
MAD-464-I Medium vol. (93 dB) |  | 0.0003 | 0 | 0 | 0.0097 | 0
MAD-464-I High vol. (97 dB) |  | 0.0003 | 0 | 0 | 0.013 | 0
MAD-465-I Low vol. (78 dB) |  | 0.0003 | 0 | 0 | 0.0065 | 0
MAD-465-I Medium vol. (93 dB) |  | 0.0003 | 0 | 0 | 0.0097 | 0
MAD-465-I High vol. (97 dB) |  | 0.0003 | 0 | 0 | 0.013 | 0
MAD-472 |  | 0.00035 | 0 | 0 | 0.014 | 0
MAD-473 |  | 0.00035 | 0 | 0 | 0.015 | 0
MAD-481 |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-490 |  | 0.0003 | 0 |  | 0.05 | 0
PAD-10 |  | 0.000625 | 0 | 0 | 0.005 | 0
PAD-10A-I |  | 0.000185 | 0 | 0 | 0.004 | 0
TPLD-100 (CCD-102) = 3 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-104) = 5 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-108) = 9 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-112) = 13 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-103) = 7 loop address |  | 0.0003 | 0 |  | 0.003 | 0
Total | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
Loop Parameters
Cu | 0.0172 |  | Ω*mm2/m
I_Standby | 0 |  | A
I_Alarm | 0 |  | A
I_Sounders | 0 |  | A
I_Total | 0 |  | A
V_Lin_Ring | 6.9 |  | V
Minimum Cable Section for common Lenghts | [10 empty] | Warning: The Minimum Cable Seccion in the Loop is 0,5 mm2
Lenghts | 1000 |  | 1500 |  |  | 2000 | 2500 | 3000 | 3500 | m
R_Cable | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
S_min | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | mm2
Maximum Cable Lenght for Standard Cable Section (IEC 60228) | [10 empty] | Warning: The Maximum Cable Length in the Loop is 3500 meters
Section | 0.5 |  | 0.75 |  |  | 1 | 1.5 | 2.5 | 4 | mm2
R_Cable | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
L_max | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | m
Maximum Current Calculation
? S | 1.5 |  | mm2
? L | 2000 |  | mm2
R_Cable_Sys | 45.8667 |  | Ω
R_eq_Ring_Sys | 22.9333 |  | Ω
I_max | 0.30087 |  | A
System Check
Current |  |  | OK
Addresses |  |  | OK
This tool may be used as a design help for Detnov Security S.L. We reserve the right not to be responsible for its accuracy, completeness or quality of the information provided, including any kind of information which could be incomplete or incorrect.

## SC_Loop 6
SYSTEM CALCULATOR DETNOV CAD-150 EXCEL TOOL | [10 empty] | SC 116 en 2019 f
Loop | [8 empty] | System Check
Section of wire | 1.5 |  | mm2 | [5 empty] | Current |  | OK
Lenght loop | 2000 |  | meters | [5 empty] | Addresses |  | OK
Fill Cable Section in mm2 and the Line Distance in meters (Yelow field)
| Fill the PCS field for the desired configuration (Yelow field) | Fill the PCS field for the desired configuration (Yelow field)
Devices Loop 6
REF. | PCS | I_Standby (A) | I_Standby (A) | PCS_alarm | I_Alarm (A) | I_Alarm (A) | I_Sounders (A) | DET | MOD | SND | ADR
DOD-220A |  | 0.0003 | 0 | 0 | 0.003 | 0
DOD-220A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DOTD-230A |  | 0.0003 | 0 | 0 | 0.003 | 0
DOTD-230A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-210A |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-210A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-215A |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-215A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DGD-600 |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-600-AC |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-620 |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-620-AC |  | 0.00091 | 0 | 0 | 0.0011 | 0
MAD-401 & MAD-401-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-402 & MAD-402-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-405-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-409-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-411 & MAD-411-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-412 & MAD-412-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-415-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-419-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-421 & MAD-421-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-422 & MAD-422-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-425-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-429-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-431 & MAD-431-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-432 & MAD-432-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-441 & MAD-441-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-442 & MAD-442-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-450 & MAD-450-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-451-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-461-I |  | 0.0003 | 0 | 0 | 0.009 | 0
MAD-464-I Low vol. (78 dB) |  | 0.0003 | 0 | 0 | 0.0065 | 0
MAD-464-I Medium vol. (93 dB) |  | 0.0003 | 0 | 0 | 0.0097 | 0
MAD-464-I High vol. (97 dB) |  | 0.0003 | 0 | 0 | 0.013 | 0
MAD-465-I Low vol. (78 dB) |  | 0.0003 | 0 | 0 | 0.0065 | 0
MAD-465-I Medium vol. (93 dB) |  | 0.0003 | 0 | 0 | 0.0097 | 0
MAD-465-I High vol. (97 dB) |  | 0.0003 | 0 | 0 | 0.013 | 0
MAD-472 |  | 0.00035 | 0 | 0 | 0.014 | 0
MAD-473 |  | 0.00035 | 0 | 0 | 0.015 | 0
MAD-481 |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-490 |  | 0.0003 | 0 |  | 0.05 | 0
PAD-10 |  | 0.000625 | 0 | 0 | 0.005 | 0
PAD-10A-I |  | 0.000185 | 0 | 0 | 0.004 | 0
TPLD-100 (CCD-102) = 3 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-104) = 5 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-108) = 9 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-112) = 13 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-103) = 7 loop address |  | 0.0003 | 0 |  | 0.003 | 0
Total | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
Loop Parameters
Cu | 0.0172 |  | Ω*mm2/m
I_Standby | 0 |  | A
I_Alarm | 0 |  | A
I_Sounders | 0 |  | A
I_Total | 0 |  | A
V_Lin_Ring | 6.9 |  | V
Minimum Cable Section for common Lenghts | [10 empty] | Warning: The Minimum Cable Seccion in the Loop is 0,5 mm2
Lenghts | 1000 |  | 1500 |  |  | 2000 | 2500 | 3000 | 3500 | m
R_Cable | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
S_min | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | mm2
Maximum Cable Lenght for Standard Cable Section (IEC 60228) | [10 empty] | Warning: The Maximum Cable Length in the Loop is 3500 meters
Section | 0.5 |  | 0.75 |  |  | 1 | 1.5 | 2.5 | 4 | mm2
R_Cable | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
L_max | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | m
Maximum Current Calculation
? S | 1.5 |  | mm2
? L | 2000 |  | mm2
R_Cable_Sys | 45.8667 |  | Ω
R_eq_Ring_Sys | 22.9333 |  | Ω
I_max | 0.30087 |  | A
System Check
Current |  |  | OK
Addresses |  |  | OK
This tool may be used as a design help for Detnov Security S.L. We reserve the right not to be responsible for its accuracy, completeness or quality of the information provided, including any kind of information which could be incomplete or incorrect.

## SC_Loop 7
SYSTEM CALCULATOR DETNOV CAD-150 EXCEL TOOL | [10 empty] | SC 116 en 2019 f
Loop | [8 empty] | System Check
Section of wire | 1.5 |  | mm2 | [5 empty] | Current |  | OK
Lenght loop | 2000 |  | meters | [5 empty] | Addresses |  | OK
Fill Cable Section in mm2 and the Line Distance in meters (Yelow field)
| Fill the PCS field for the desired configuration (Yelow field) | Fill the PCS field for the desired configuration (Yelow field)
Devices Loop 7
REF. | PCS | I_Standby (A) | I_Standby (A) | PCS_alarm | I_Alarm (A) | I_Alarm (A) | I_Sounders (A) | DET | MOD | SND | ADR
DOD-220A |  | 0.0003 | 0 | 0 | 0.003 | 0
DOD-220A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DOTD-230A |  | 0.0003 | 0 | 0 | 0.003 | 0
DOTD-230A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-210A |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-210A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-215A |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-215A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DGD-600 |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-600-AC |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-620 |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-620-AC |  | 0.00091 | 0 | 0 | 0.0011 | 0
MAD-401 & MAD-401-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-402 & MAD-402-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-405-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-409-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-411 & MAD-411-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-412 & MAD-412-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-415-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-419-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-421 & MAD-421-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-422 & MAD-422-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-425-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-429-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-431 & MAD-431-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-432 & MAD-432-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-441 & MAD-441-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-442 & MAD-442-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-450 & MAD-450-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-451-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-461-I |  | 0.0003 | 0 | 0 | 0.009 | 0
MAD-464-I Low vol. (78 dB) |  | 0.0003 | 0 | 0 | 0.0065 | 0
MAD-464-I Medium vol. (93 dB) |  | 0.0003 | 0 | 0 | 0.0097 | 0
MAD-464-I High vol. (97 dB) |  | 0.0003 | 0 | 0 | 0.013 | 0
MAD-465-I Low vol. (78 dB) |  | 0.0003 | 0 | 0 | 0.0065 | 0
MAD-465-I Medium vol. (93 dB) |  | 0.0003 | 0 | 0 | 0.0097 | 0
MAD-465-I High vol. (97 dB) |  | 0.0003 | 0 | 0 | 0.013 | 0
MAD-472 |  | 0.00035 | 0 | 0 | 0.014 | 0
MAD-473 |  | 0.00035 | 0 | 0 | 0.015 | 0
MAD-481 |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-490 |  | 0.0003 | 0 |  | 0.05 | 0
PAD-10 |  | 0.000625 | 0 | 0 | 0.005 | 0
PAD-10A-I |  | 0.000185 | 0 | 0 | 0.004 | 0
TPLD-100 (CCD-102) = 3 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-104) = 5 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-108) = 9 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-112) = 13 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-103) = 7 loop address |  | 0.0003 | 0 |  | 0.003 | 0
Total | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
Loop Parameters
Cu | 0.0172 |  | Ω*mm2/m
I_Standby | 0 |  | A
I_Alarm | 0 |  | A
I_Sounders | 0 |  | A
I_Total | 0 |  | A
V_Lin_Ring | 6.9 |  | V
Minimum Cable Section for common Lenghts | [10 empty] | Warning: The Minimum Cable Seccion in the Loop is 0,5 mm2
Lenghts | 1000 |  | 1500 |  |  | 2000 | 2500 | 3000 | 3500 | m
R_Cable | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
S_min | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | mm2
Maximum Cable Lenght for Standard Cable Section (IEC 60228) | [10 empty] | Warning: The Maximum Cable Length in the Loop is 3500 meters
Section | 0.5 |  | 0.75 |  |  | 1 | 1.5 | 2.5 | 4 | mm2
R_Cable | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
L_max | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | m
Maximum Current Calculation
? S | 1.5 |  | mm2
? L | 2000 |  | mm2
R_Cable_Sys | 45.8667 |  | Ω
R_eq_Ring_Sys | 22.9333 |  | Ω
I_max | 0.30087 |  | A
System Check
Current |  |  | OK
Addresses |  |  | OK
This tool may be used as a design help for Detnov Security S.L. We reserve the right not to be responsible for its accuracy, completeness or quality of the information provided, including any kind of information which could be incomplete or incorrect.

## SC_Loop 8
SYSTEM CALCULATOR DETNOV CAD-150 EXCEL TOOL | [10 empty] | SC 116 en 2019 f
Loop | [8 empty] | System Check
Section of wire | 1.5 |  | mm2 | [5 empty] | Current |  | OK
Lenght loop | 2000 |  | meters | [5 empty] | Addresses |  | OK
Fill Cable Section in mm2 and the Line Distance in meters (Yelow field)
| Fill the PCS field for the desired configuration (Yelow field) | Fill the PCS field for the desired configuration (Yelow field)
Devices Loop 8
REF. | PCS | I_Standby (A) | I_Standby (A) | PCS_alarm | I_Alarm (A) | I_Alarm (A) | I_Sounders (A) | DET | MOD | SND | ADR
DOD-220A |  | 0.0003 | 0 | 0 | 0.003 | 0
DOD-220A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DOTD-230A |  | 0.0003 | 0 | 0 | 0.003 | 0
DOTD-230A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-210A |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-210A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-215A |  | 0.0003 | 0 | 0 | 0.003 | 0
DTD-215A-I |  | 0.0003 | 0 | 0 | 0.003 | 0
DGD-600 |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-600-AC |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-620 |  | 0.00091 | 0 | 0 | 0.0011 | 0
DGD-620-AC |  | 0.00091 | 0 | 0 | 0.0011 | 0
MAD-401 & MAD-401-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-402 & MAD-402-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-405-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-409-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-411 & MAD-411-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-412 & MAD-412-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-415-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-419-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-421 & MAD-421-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-422 & MAD-422-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-425-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-429-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-431 & MAD-431-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-432 & MAD-432-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-441 & MAD-441-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-442 & MAD-442-I |  | 0.0003 | 0 | 0 | 0.003 | 0 |  |  | 0
MAD-450 & MAD-450-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-451-I |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-461-I |  | 0.0003 | 0 | 0 | 0.009 | 0
MAD-464-I Low vol. (78 dB) |  | 0.0003 | 0 | 0 | 0.0065 | 0
MAD-464-I Medium vol. (93 dB) |  | 0.0003 | 0 | 0 | 0.0097 | 0
MAD-464-I High vol. (97 dB) |  | 0.0003 | 0 | 0 | 0.013 | 0
MAD-465-I Low vol. (78 dB) |  | 0.0003 | 0 | 0 | 0.0065 | 0
MAD-465-I Medium vol. (93 dB) |  | 0.0003 | 0 | 0 | 0.0097 | 0
MAD-465-I High vol. (97 dB) |  | 0.0003 | 0 | 0 | 0.013 | 0
MAD-472 |  | 0.00035 | 0 | 0 | 0.014 | 0
MAD-473 |  | 0.00035 | 0 | 0 | 0.015 | 0
MAD-481 |  | 0.0003 | 0 | 0 | 0.003 | 0
MAD-490 |  | 0.0003 | 0 |  | 0.05 | 0
PAD-10 |  | 0.000625 | 0 | 0 | 0.005 | 0
PAD-10A-I |  | 0.000185 | 0 | 0 | 0.004 | 0
TPLD-100 (CCD-102) = 3 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-104) = 5 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-108) = 9 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-112) = 13 loop address |  | 0.0003 | 0 |  | 0.003 | 0
TPLD-100 (CCD-103) = 7 loop address |  | 0.0003 | 0 |  | 0.003 | 0
Total | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
Loop Parameters
Cu | 0.0172 |  | Ω*mm2/m
I_Standby | 0 |  | A
I_Alarm | 0 |  | A
I_Sounders | 0 |  | A
I_Total | 0 |  | A
V_Lin_Ring | 6.9 |  | V
Minimum Cable Section for common Lenghts | [10 empty] | Warning: The Minimum Cable Seccion in the Loop is 0,5 mm2
Lenghts | 1000 |  | 1500 |  |  | 2000 | 2500 | 3000 | 3500 | m
R_Cable | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
S_min | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | mm2
Maximum Cable Lenght for Standard Cable Section (IEC 60228) | [10 empty] | Warning: The Maximum Cable Length in the Loop is 3500 meters
Section | 0.5 |  | 0.75 |  |  | 1 | 1.5 | 2.5 | 4 | mm2
R_Cable | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
R_eq_Ring | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | Ω
L_max | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | m
Maximum Current Calculation
? S | 1.5 |  | mm2
? L | 2000 |  | mm2
R_Cable_Sys | 45.8667 |  | Ω
R_eq_Ring_Sys | 22.9333 |  | Ω
I_max | 0.30087 |  | A
System Check
Current |  |  | OK
Addresses |  |  | OK
This tool may be used as a design help for Detnov Security S.L. We reserve the right not to be responsible for its accuracy, completeness or quality of the information provided, including any kind of information which could be incomplete or incorrect.